{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":159,"n_cols":7,"rows_kept":159,"cut":false,"hidden":false,"merged":[[149,0,149,7],[0,0,0,6],[53,0,53,7],[62,0,62,7],[97,1,97,7],[114,0,114,6],[7,0,7,7],[6,0,6,7]]}
["Оперативная информация по отключениям в сетях 6/10 кВ за IV квартал 2013 года."]
[]
[]
[null,null,"Наименование","Наименование поврежденной линии,","время",null,"Дефект"]
[null,null,"№ п/ст, РП, ТП"," оборудования"]
["№","ДАТА",null,"6-10 кВ"," Откл.","вкл"]
["4 КВАРТАЛ 2010 года"]
["Великий Новгород IV квартал 2013 года."]
[1,"2013-10-07","ТП - 629 откл. ВВ на РП - 36","ВЛ 6 кВ РП - 36 - ТП - 629","2013-10-07T10:59:00","2013-10-07T12:24:00","птица на ВЛ"]
[2,"2013-10-09","ПС \"Западная\" яч.ф.03","концевая муфта ф. 03","2013-10-09T06:08:00","2013-10-09T06:34:00","пробой изоляции"]
[3,"2013-10-17","РП - 20 откл.МВ на ТП  - 363",null,"2013-10-17T05:26:00","2013-10-17T05:26:00","работа АВР"]
[4,"2013-10-18","ПС \"Базовая\" \"земля\" ф.37","КЛ 6кВ ТП - 172 - РП - 16","2013-10-17T21:52:00","2013-10-17T22:33:00","пробой изоляции"]
[5,"2013-10-21","ПС \"ЖБИ\" откл. ф.03","л/р ВЛ 6 кВ на ТП - 650","2013-10-21T12:40:00","2013-10-21T13:55:00","пробой опорного изолятора "]
[6,"2013-10-29","ПС \"Районная\" откл. МВ ф.38","КЛ 6 кВ РП - 24 - ТП - 431","2013-10-29T12:35:00","2013-10-29T13:26:00","пробой изоляции"]
[7,"2013-10-29","РП - 42 откл. ВВ на ТП - 202","ВЛ 6 кВ ТП - 10 - ТП - 164","2013-10-29T13:30:00","2013-10-29T15:05:00","штормовой ветер"]
[8,"2013-10-29","ТП - 172 откл. ВВ на РП - 16","ВЛ 6 кВ п/п 31 - ТП - 267","2013-10-29T13:40:00","2013-10-29T17:40:00","повреждение опоры"]
[9,"2013-10-29","ПС \"Рышево\" откл. Л - 3","ВЛ 10 кВ","2013-10-29T14:10:00","2013-10-29T16:30:00","в сетях МРСК"]
[10,"2013-10-29","ПС \"Дубровка\" \"земля\" на Л - 4","ВЛ 10 кВ л/р 130 - ТП - 599","2013-10-29T16:00:00","2013-10-29T19:30:00","обрыв провода"]
[11,"2013-11-01","РП - 3 откл. МВ на ТП - 473","КЛ 6 кВ ТП - 240 - ТП - 69","2013-11-01T17:25:00","2013-11-01T18:28:00","пробой изоляции"]
[12,"2013-11-04","ТП - 172 откл. ВВ на РП - 16","КЛ - ВЛ 6 кВ","2013-11-04T14:27:00","2013-11-04T16:21:00","штормовой ветер"]
[13,"2013-11-04","ПС \"Мостищи\" откл. МВ ф.03","ТП \"Метер\"","2013-11-04T14:27:00","2013-11-05T01:03:00","сети абонента"]
[14,"2013-11-04","ПС \"Западная\" яч.ф.14, 31",null,"2013-11-04T14:30:00","2013-11-04T15:23:00","в сетях МРСК"]
[15,"2013-11-04","ПС \"Мостищи\" откл. МВ ф.07","КЛ - ВЛ 10 кВ","2013-11-04T18:01:00","2013-11-04T19:23:00","штормовой ветер"]
[16,"2013-11-04","РП - 27 откл. МВ на ТП - 119","КЛ - ВЛ 6 кВ","2013-11-04T18:55:00","2013-11-04T20:50:00","штормовой ветер"]
[17,"2013-11-04","ТП - 172 откл. ВВ на РП - 16","ВЛ 6 кВ п/п 31 - ТП - 267","2013-11-04T18:00:00","2013-11-04T20:35:00","дерево на ВЛ"]
[18,"2013-11-04","ПС \"Пролетарий\"","ВЛ 35 кВ","2013-11-04T18:00:00","2013-11-05T01:00:00","в сетях МРСК"]
[19,"2013-11-05","ПС \"Мостищи\" откл. МВ ф.42","КЛ - ВЛ 10 кВ","2013-11-05T02:51:00","2013-11-05T03:04:00","штормовой ветер"]
[20,"2013-11-05","ПС \"Западная\" откл. Т-2","Т - 2","2013-11-05T04:29:00","2013-11-05T05:00:00","в сетях МРСК"]
[21,"2013-11-05","ПС \"Районная\" откл. МВ ф.28","КЛ 6 кВ ПС \"Районная\" - РП - 47, ф.28","2013-11-05T18:00:00","2013-11-05T18:40:00","пробой изоляции"]
[22,"2013-11-10","ПС \"Мостищи\" откл. МВ ф.39","КЛ 10 кВ ПС \"Мостищи\" - РП - 5, ф.39","2013-11-10T14:50:00","2013-11-10T15:35:00","пробой изоляции"]
[23,"2013-11-10","ПС \"Районная\" откл. МВ ф.06","КЛ 6 кВ ПС \"Районная\" - РП - 7, ф.06","2013-11-10T19:03:00","2013-11-10T19:03:00","пробой изоляции"]
[24,"2013-11-11","ПС \"Районная\" откл. секция Т - 1","КЛ 6 кВ ПС \"Районная\" - РП - 7, ф.15","2013-11-11","2013-11-11T02:03:00","пробой изоляции"]
[25,"2013-11-14","РП - 24 откл. МВ на ТП - 359","КЛ 6 кВ ТП - 359 - ТП - 264","2013-11-14T19:52:00","2013-11-14T23:15:00","пробой изоляции"]
[26,"2013-11-14","РП - 24 откл. МВ на ТП - 359","КЛ 6 кВ ТП - 354 -ТП - 6","2013-11-14T19:52:00","2013-11-14T23:15:00","пробой изоляции"]
[27,"2013-11-16","РП - 25 откл. МВ на ТП - 409","каб. разделка 10 кВ ТП - 409 - на ТП - 263","2013-11-16T02:25:00","2013-11-16T03:08:00","пробой изоляции"]
[28,"2013-11-16","РП - 3 откл. МВ на ТП - 473","КЛ 6 кВ ТП - 473 - ТП - 240","2013-11-16T12:51:00","2013-11-16T14:11:00","пробой изоляции"]
[29,"2013-11-17","ПС \"Рышево\" откл. Л - 3, ПС \"Новоселицы\" отл. Л - 6","ВЛ 10 ","2013-11-17T21:30:00","2013-11-17T22:00:00","обрыв провода"]
[30,"2013-11-28","ПС \"Насосная\" откл. МВ ф.04","каб. выход 10 кВ с ТП - 166 на ВЛ 10 кВ ф.04","2013-11-28T03:10:00","2013-11-28T04:18:00","пробой изоляции"]
[31,"2013-11-30","ПС \"Районная\" откл. МВ ф.06","КЛ 6 кВ ПС \"Районная\" - РП - 7, ф.06","2013-11-30T19:15:00","2013-11-30T19:15:00","пробой изоляции"]
[32,"2013-12-02","ПС \"Пролетарий\" откл. Л - 2","ВЛ 10 кВ","2013-12-02T05:30:00","2013-12-02T10:20:00","дерево на ВЛ"]
[33,"2013-12-04","РП - 25 откл. МВ на ТП - 379","КЛ 6 кВ РП - 25 - ТП - 379","2013-12-04T17:20:00","2013-12-04T18:26:00","пробой изоляции"]
[34,"2013-12-06","РП - 42 откл. МВ на ТП - 202","ВЛ 6 кВ ТП - 164 - п/п 5","2013-12-06T19:27:00","2013-12-06T20:05:00","дерево на ВЛ"]
[35,"2013-12-07","ПС \"Савино\" откл. Л - 3","ВЛ 10 кВ л/р 130 - ТП - 599","2013-12-07T10:00:00","2013-12-07T15:00:00","обрыв провода"]
[36,"2013-12-08","ТП - 5 откл. МВ ф.27","КЛ 10 кВ ТП - 2 - ТП - 36","2013-12-08T19:22:00","2013-12-08T19:45:00","пробой изоляции"]
[37,"2013-12-10","ТП - 5 откл. МВ ф.05","КЛ 10 кВ ТП - 2 - ТП - 36","2013-12-10T05:40:00","2013-12-10T06:45:00","пробой изоляции"]
[38,"2013-12-10","ПС \"Районная\" откл. МВ ф.28","КЛ 10 кВ ТП - 464 - РП - 24","2013-12-10T22:38:00","2013-12-10T23:18:00","пробой изоляции"]
[39,"2013-12-10","ПС \"Районная\" откл. МВ ф.46","РП - 27 ячейка на ТП - 396","2013-12-10T22:38:00","2013-12-10T23:54:00","повреждение оборудования"]
[40,"2013-12-13","РП - 27 откл. МВ на ТП - 119","ТП - 487","2013-12-13T06:10:00","2013-12-13T08:43:00","повреждение трансформатора"]
[41,"2013-12-13","ТП - 5 откл. МВ ф.27","КЛ 10 кВ ТП - 2 - ТП - 5","2013-12-13T13:50:00","2013-12-13T15:00:00","пробой изоляции"]
[42,"2013-12-18","ПС \"Районная\" откл. МВ ф.28","КЛ 6 кВ ПС \"Районная\" РП - 47, ф.28","2013-12-18T18:13:00","2013-12-18T18:34:00","пробой изоляции"]
[43,"2013-12-22","ПС \"ЖБИ\" откл. МВ ф. 2","КЛ 6 кВ ТП - 154 - ТП - 50","2013-12-22T06:15:00","2013-12-22T07:10:00","повреждение концевой воронки"]
[44,"2013-12-26","РП - 5 откл. МВ на ТП - 248","КЛ 10 кВ ТП - 248 - ТП - 519","2013-12-26T08:15:00","2013-12-26T09:20:00","пробой изоляции"]
[]
["ЧУДОВСКИЙ ФИЛИАЛ IV квартал 2013 года"]
[1,"2013-10-05","ПС \"Вишерская\" откл. Л - 18","КЛ - ВЛ 10 кВ ","2013-10-05T13:31:00","2013-10-05T13:34:00","работа РЗА"]
[2,"2013-10-24","ПС \"Чудово\" откл. Л - 16","ТП - 47","2013-10-24T00:45:00","2013-10-24T02:03:00","животное в ТП"]
[3,"2013-10-29","ПС \"Чудово\" откл. Л - 13","ВЛ 10 кВ ","2013-10-29T14:09:00","2013-10-29T15:10:00","штормовой ветер"]
[4,"2013-10-29","ПС \"Вишерская\" откл. Л - 6","ВЛ 10 кВ ","2013-10-29T14:27:00","2013-10-29T14:55:00","штормовой ветер"]
[5,"2013-11-04","ПС \"Чудово\" откл. Л - 13","ВЛ 10 кВ ","2013-11-04T20:04:00","2013-11-04T20:45:00","штормовой ветер"]
[6,"2013-11-04","ПС \"Вишерская\" откл. Л - 18","ВЛ 10 кВ ","2013-11-04T20:30:00","2013-11-04T20:40:00","штормовой ветер"]
[7,"2013-12-13","ПС \"Чудово\" откл. Л - 5","ВЛ 10 кВ ","2013-12-13T10:52:00","2013-12-13T11:00:00","отгорел шлейф"]
[]
["ОКУЛОВСКИЙ ФИЛИАЛ  IV квартал 2013 года"]
[]
[1,"2013-10-09","ПС \"Окуловка\" откл. Л - 6","КЛ - ВЛ 10 кВ ","2013-10-09T09:50:00","2013-10-09T09:57:00","работа РЗА"]
[2,"2013-10-09","ПС \"Окуловка\" откл. Л - 5","КЛ 10 кВ ТП - 96 - ТП - 72","2013-10-09T04:50:00","2013-10-09T05:50:00","пробой изоляции"]
[3,"2013-10-11","ПС \"Окуловка\" откл. Л - 38","ВЛ 10 кВ ","2013-10-11T20:02:00","2013-10-11T22:11:00","наброс на ВЛ"]
[4,"2013-10-11","ПС \"Окуловка\" откл. Л - 6","ТП - 25","2013-10-11T20:29:00","2013-10-11T21:30:00","повреждение ведомственной подстанции"]
[5,"2013-10-11","ПС \"Окуловка\" откл. Л - 18","ВЛ 10 кВ ","2013-10-11T21:16:00","2013-10-12T12:00:00","наброс на ВЛ"]
[6,"2013-10-13","ПС \"Окуловка\" откл. Л - 6","ВЛ 10 кВ ","2013-10-13T22:29:00","2013-10-13T22:31:00","работа РЗА"]
[7,"2013-10-22","ПС \"Любытино\" откл. Л - 11 \"земля\"","ВЛ 10 кВ ","2013-10-22T10:05:00","2013-10-22T10:25:00","ветка на ВЛ"]
[8,"2013-10-24","ПС \"Кулотино\" откл. Л - 3","ТП - 7","2013-10-24T14:15:00","2013-10-24T14:35:00","работа РЗА"]
[9,"2013-10-29","ПС \"Кулотино\" откл. Л - 3","ВЛ 10 кВ ","2013-10-29T10:20:00","2013-10-29T11:20:00","падение дерева"]
[10,"2013-10-29","ПС \"Крестцы\" откл. Л - 1","ВЛ 10 кВ ","2013-10-29T14:10:00","2013-10-29T15:45:00","штормовой ветер"]
[11,"2013-10-29","ПС \"Крестцы\" откл. Л - 11","ВЛ 10 кВ ","2013-10-29T14:20:00","2013-10-29T16:40:00","штормовой ветер"]
[12,"2013-10-29","ПС \"Крестцы\" откл. Л - 6","ВЛ 10 кВ ","2013-10-29T15:15:00","2013-10-29T16:45:00","штормовой ветер"]
[13,"2013-10-29","ПС \"Окуловка\" откл. Л - 6","ВЛ 10 кВ ","2013-10-29T15:00:00","2013-10-29T15:19:00","штормовой ветер"]
[14,"2013-10-31","ПС \"Окуловка\" откл. Л - 2","ВЛ 10 кВ ","2013-10-31T15:19:00","2013-10-31T15:26:00","дерево на ВЛ"]
[15,"2013-11-04","ПС \"Угловка\" откл. Л - 3.","ВЛ 10 кВ ","2013-11-04T11:10:00","2013-11-04T11:15:00","штормовой ветер"]
[16,"2013-11-04","ПС \"Угловка\" откл. Л - 9.","ВЛ 10 кВ ","2013-11-04T12:11:00","2013-11-04T12:18:00","штормовой ветер"]
[17,"2013-11-04","ПС \"Угловка\" откл. Л - 3","ВЛ 10 кВ ","2013-11-04T13:25:00","2013-11-04T13:31:00","штормовой ветер"]
[18,"2013-11-04","ПС \"Угловка\" откл. Л - 9.","ВЛ 10 кВ ","2013-11-04T14:43:00","2013-11-04T16:31:00","штормовой ветер"]
[19,"2013-11-04","ПС \"Угловка\" откл. Л - 3.","ВЛ 10 кВ ","2013-11-04T15:03:00","2013-11-04T15:18:00","штормовой ветер"]
[20,"2013-11-04","ПС \"Окуловка\" откл. Л - 6","ВЛ 10 кВ ","2013-11-04T16:55:00","2013-11-04T20:38:00","штормовой ветер"]
[21,"2013-11-04","ПС \"Угловка\" откл. Л - 3","ВЛ 10 кВ ","2013-11-04T20:45:00","2013-11-04T21:10:00","штормовой ветер"]
[22,"2013-11-04","ПС \"Угловка\" откл. Л - 3","ВЛ 10 кВ ","2013-11-04T21:25:00","2013-11-04T22:10:00","штормовой ветер"]
[23,"2013-11-04","ПС \"Крестцы\" откл. Л - 11","ВЛ 10 кВ ","2013-11-04T14:26:00","2013-11-04T14:50:00","штормовой ветер"]
[24,"2013-11-04","ПС \"Крестцы\" откл. Л - 1,6,7,11","ВЛ 10 кВ ","2013-11-04T17:10:00","2013-11-04T17:37:00","штормовой ветер"]
[25,"2013-11-04","ПС \"Крестцы\" откл. Л - 11","ВЛ 10 кВ ","2013-11-04T18:47:00","2013-11-04T18:55:00","штормовой ветер"]
[26,"2013-11-30","ПС \"Крестцы\" откл. Л - 12","ВЛ 10 кВ ","2013-11-30T16:22:00","2013-11-30T22:07:00","дерево на ВЛ"]
[27,"2013-12-02","ПС \"Крестцы\" откл. Л - 1","ВЛ 10 кВ ","2013-12-02T06:40:00","2013-12-02T08:46:00","дерево на ВЛ"]
[28,"2013-12-06","ПС \"Крестцы\" откл. Л - 11","ВЛ 10 кВ ","2013-12-06T21:33:00","2013-12-06T21:55:00","дерево на ВЛ"]
[29,"2013-12-06","ПС \"Крестцы\" откл Л - 11","ВЛ 10 кВ ","2013-12-06T22:45:00","2013-12-06T23:10:00","дерево на ВЛ"]
[30,"2013-12-09","ПС \"Угловка\" откл. Л - 6","КЛ 10 кВ ПС \"Угловка\" - л/р 2","2013-12-09T16:26:00","2013-12-09T16:36:00","пробой изоляции"]
[31,"2013-12-12","ПС \"Окуловка-330\" откл. Л-5","ВЛ 10 кВ ТП - 14 - ТП - 71","2013-12-12T04:21:00","2013-12-12T05:57:00","налипание снега"]
[32,"2013-12-13","ПС \"Окуловка\" откл. Л - 6","ВЛ 10 кВ  ТП - 26 - ТП - 45","2013-12-13T04:50:00","2013-12-13T05:10:00","пробой штыревого изолятора"]
[]
[null,"ВАЛДАЙСКИЙ ФИЛИАЛ IV квартал 2013 года."]
[1,"2013-10-17","ПС \"Валдай\"  Л - 7 \"земля\"","КЛ 10 кВ ТП - 55 - ТП - 35","2013-10-17","2013-10-19T19:00:00","пробой изоляции"]
[2,"2013-10-24","ПС \"Валдай\"  Л - 7","КЛ 10 кВ ТП - 5 - ТП - 36","2013-10-24T21:09:00","2013-10-24T23:35:00","пробой изоляции"]
[3,"2013-10-26","ПС\"Валдай\" откл. Л - 2","ТП - 46","2013-10-26T22:10:00","2013-10-26T22:37:00","повреждение ведомственной подстанции"]
[4,"2013-10-29","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-10-29T12:45:00","2013-10-29T13:15:00","штормовой ветер"]
[5,"2013-10-29","ПС \"Марево\" откл. Л - 6","ВЛ 10 кВ ","2013-10-29T12:40:00","2013-10-29T13:35:00","падение дерева"]
[6,"2013-10-29","ПС \"Марево\" откл. Л - 3","ВЛ 10 кВ ","2013-10-29T16:45:00","2013-10-29T17:10:00","падение дерева"]
[7,"2013-11-04","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-11-04T16:40:00","2013-11-04T16:50:00","падение дерева"]
[8,"2013-12-02","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-12-02T07:15:00","2013-12-02T07:25:00","штормовой ветер"]
[9,"2013-12-05","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-12-05T03:40:00","2013-12-05T05:00:00","налипание снега"]
[10,"2013-12-05","ПС \"Валдай\"  Л - 7","КЛ 10 кВ ТП - 35 - ТП - 6","2013-12-05T21:07:00","2013-12-05T23:15:00","пробой изоляции"]
[11,"2013-12-07","ПС \"Валдай\" откл. Л - 4","ВЛ 10 кВ ","2013-12-07T14:50:00","2013-12-07T17:20:00","обрыв провода"]
[12,"2013-12-10","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-12-10T21:00:00","2013-12-10T21:40:00","не обнаружено"]
[13,"2013-12-12","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-12-12T15:00:00","2013-12-12T21:40:00","обрыв провода"]
[14,"2013-12-16","ПС \"Лычково\" откл. Л - 2","ВЛ 10 кВ ","2013-12-16T19:30:00","2013-12-16T19:50:00","работа РЗА"]
[15,"2013-12-21","ПС \"Марево\" откл. Л - 6","ВЛ 10 кВ ","2013-12-21T18:00:00","2013-12-21T19:40:00","пробой проходного изолятора"]
[]
["БОРОВИЧСКИЙ ФИЛИАЛ IV квартал 2013 года."]
[]
[1,"2013-10-05","ПС \"Любытино\" откл. Л - 11","ТП - 3","2013-10-05T23:15:00","2013-10-05T23:43:00","животное на оборудовании"]
[2,"2013-10-09","ТП - 27 РУ 10 кВ ","сгорели 2 ПК","2013-10-09T21:50:00","2013-10-09T23:50:00","работа РЗА"]
[3,"2013-10-19","ПС \"Пестово\" откл. Л - 2","ВЛ 10 кВ","2013-10-19T05:43:00","2013-10-19T08:25:00","ветка на ВЛ"]
[4,"2013-10-25","ПС \"Пестово\" откл. Л - 2","КЛ 10 кВ ТП - 1 - ТП - 25","2013-10-25T00:02:00","2013-10-25T01:58:00","пробой изоляции"]
[5,"2013-10-25","ПС \"Любытино\" откл. Л - 11","ТП - 13","2013-10-25T23:30:00","2013-10-26T03:08:00","повреждение разрядника"]
[6,"2013-10-25","ТП - 29","ВЛ 10 кВ","2013-10-26T12:00:00","2013-10-26T16:25:00","отгорел шлейф на л/р"]
[7,"2013-10-28","ПС \"Огнеупоры\" откл. Л Боровичи-4","КЛ 6 кВ ТП - 48 - ТП - 167","2013-10-28T17:20:00","2013-10-28T17:40:00","пробой изоляции"]
[8,"2013-10-28","ПС \"Огнеупоры\" откл. Л Боровичи-3","КЛ 6 кВ ТП - 2 - ТП - 159","2013-10-28T17:30:00","2013-10-28T19:40:00","пробой изоляции"]
[9,"2013-10-29","ТП - 123 откл. МВ ф. Боровичи - 6","ВЛ 10 кВ","2013-10-29T13:06:00","2013-10-29T14:03:00","штормовой ветер"]
[10,"2013-10-29","РП - 7 откл. яч. 3,7","ВЛ 10 кВ","2013-10-29T13:13:00","2013-10-29T13:45:00","штормовой ветер"]
[11,"2013-10-29","ТП - 129 откл. МВ на ТП - 101","ВЛ 10 кВ","2013-10-29T13:41:00","2013-10-29T14:10:00","штормовой ветер"]
[12,"2013-10-29","ТП - 129 откл. МВ на ТП - 101","ВЛ 10 кВ","2013-10-29T14:45:00","2013-10-29T15:15:00","штормовой ветер"]
[13,"2013-10-29","ТП - 123 откл. МВ ф. Боровичи - 6","ВЛ 10 кВ","2013-10-29T15:00:00","2013-10-29T16:13:00","штормовой ветер"]
[14,"2013-10-29","ПС \"Любытино\" откл. Л - 11","ВЛ 10 кВ","2013-10-29T11:50:00","2013-10-29T14:50:00","штормовой ветер"]
[15,"2013-10-29","ПС \"Пестово\" откл. Л - 2","ВЛ 10 кВ","2013-10-29T14:30:00","2013-10-29T15:53:00","штормовой ветер"]
[16,"2013-10-29","ПС \"Хвойная\" откл. Л - 4","ВЛ 10 кВ","2013-10-29T15:15:00","2013-10-29T17:35:00","штормовой ветер"]
[17,"2013-10-29","ПС \"Мошенское\" откл. Л - 1,6,8","ВЛ 110 кВ","2013-10-29T16:32:00","2013-10-29T18:22:00","в сетях МРСК"]
[18,"2013-11-04","ТП - 123 откл. МВ ф. Боровичи - 6","ВЛ 10 кВ","2013-11-04T15:35:00","2013-11-04T15:45:00","штормовой ветер"]
[19,"2013-11-04","РП - 5 откл. Л - 14","ВЛ 10 кВ ТП - 153 - ТП - 132","2013-11-04T21:15:00","2013-11-04T22:12:00","штормовой ветер"]
[20,"2013-11-04","РП - 7 откл. МВ Л - 16","ВЛ 10 кВ  ","2013-11-04T21:20:00","2013-11-04T22:03:00","штормовой ветер"]
[21,"2013-11-05","РП - 1 откл. МВ Л - 12","ВЛ 10 кВ","2013-11-05T01:58:00","2013-11-05T02:12:00","штормовой ветер"]
[22,"2013-11-05","ТП - 129 откл. МВ на ТП - 43","КЛ 10 кВ РП - 26 - ТП - 46","2013-11-05T23:05:00","2013-11-05T23:20:00","пробой изоляции"]
[23,"2013-11-05","РП - 9 откл. МВ яч. № 8","КЛ 10 кВ РП - 9 - ТП - 147","2013-11-05T01:58:00","2013-11-05T02:10:00","пробой изоляции"]
[24,"2013-11-06","ПС \"Хвойная\" откл. Л - 2","ВЛ 10 кВ","2013-11-06T14:00:00","2013-11-06T16:45:00","работа РЗА"]
[25,"2013-11-06","РП - 5 откл. МВ Л - 7","КЛ 10 кВ ТП - 12 - ТП - 65","2013-11-06T09:45:00","2013-11-06T13:00:00","пробой изоляции"]
[26,"2013-11-06","РП - 1 откл. МВ Л - 11","КЛ 10 кВ ТП - 165 - ТП - 178","2013-11-06T09:45:00","2013-11-06T11:45:00","работа РЗА"]
[27,"2013-11-30","ПС \"Неболичи\" откл. Л - 5","ВЛ 10 кВ","2013-11-30T22:55:00","2013-11-30T23:15:00","работа РЗА"]
[28,"2013-12-04","ПС \"Огнеупоры\" откл. Ф.Боровичи - 5","КЛ 10 кВ ПС \"Огнеупоры\"  - ТП - 1","2013-12-04T17:27:00","2013-12-04T18:10:00","пробой изоляции"]
[29,"2013-12-13","ПС \"Огнеупоры\" откл. МВ ф.Боровичи -1","ВЛ 10 кВ","2013-12-13T16:05:00","2013-12-13T16:44:00","штормовой ветер"]
[30,"2013-12-13","ПС \"Огнеупоры\" откл. МВ ф.Боровичи -1","ВЛ 10 кВ","2013-12-13T17:15:00","2013-12-13T17:55:00","штормовой ветер"]
[31,"2013-12-16","ПС \"Посад\" откл. Л - 2",null,"2013-12-17T03:44:00","2013-12-17T04:33:00","в сетях МРСК"]
[32,"2013-12-24","ТП - 129 откл. МВ на ТП - 43","КЛ 10 кВ ТП - 43 - ТП - 113","2013-12-24T08:00:00","2013-12-24T09:25:00","пробой изоляции"]
[]
["СТАРОРУССКИЙ ФИЛИАЛ IV квартал 2013 года"]
[]
[1,"2013-10-09","ПС \"Русса\" откл. Л - 20","КЛ 10 кВ ТП - 96 - ТП - 72","2013-10-09T04:50:00","2013-10-09T05:50:00","пробой изоляции"]
[2,"2013-10-24","РП - 2 откл. МВ на ТП - 95, Л - 8","КЛ 10 кВ ТП - 95 - ТП - 1","2013-10-24T09:48:00","2013-10-24T10:46:00","пробой изоляции"]
[3,"2013-10-27","ПС \"Русса\" откл. Л - 2","ТП - 19","2013-10-27T06:50:00","2013-10-27T12:17:00","повр. проход. изоляторов"]
[4,"2013-10-27","ПС \"Шелонь\" откл. Л - 2","ТП - 10","2013-10-27T13:25:00","2013-10-27T14:10:00","повр. проход. изоляторов"]
[5,"2013-11-30","РП - 2 откл. МВ на ТП -8","КЛ 10 ТП - 75 - ТП - 74","2013-11-30T00:10:00","2013-11-30T01:04:00","пробой изоляции"]
[6,"2013-12-13","ПС \"Шимск\"  - ТП - 15","ВЛ 10 кВ","2013-12-13T19:30:00","2013-12-13T21:14:00","отгорел шлейф"]
[7,"2013-12-16","ПС \"Русса\" откл. Л - 20","КЛ 10 кВ ТП - 96 - ТП - 72","2013-12-16T18:05:00","2013-12-16T19:34:00","пробой изоляции"]
[8,"2013-12-22","ПС \"Холм\" откл. Л - 7","ВЛ 10 кВ","2013-12-22T04:00:00","2013-12-22T06:17:00","отгорел шлейф"]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}